                                                                                         P O W E R   S U P P L Y  

                                                                                                              TEST REPORT 

Model  No :  LV10020N           Sr.No  : 220317/0713                    Date :  01/04/2022
Customer  :  Coslight India Telecom Pvt Ltd  Una HP
Special Features :    CC/CV Power Supply with digital meters

                                   Fully protected against short circuit, overloads & over voltage
Input Volts:    230V+/-10%         

Output Volts : 0-100.0V DC                           Amp Rating : 20.00Amp DC

Max Set Voltage & Range :  Tested  o.k

Load Regulation:   CC:+/- 0.05%+/- 10mA      Line Regulation : CC:+/- 0.05%+/-10mA
                                CV: +/-0.01%+/-2mV DC                                  CV:+/-0.01%+/-2mV
                                                        (for +/-10% change in line voltage)

Meter Calibration (DPM) :      Tested o.k (within +/-0.1%+/-3counts)
Indication/Controls :      Tested o.k

Short circuit & over load/overvoltage Protection : Tested o.k

Load at which tested:  20.10Amp    Volts : 100.0V DC        Hrs  : 3 hrs

Ref. Meter used for calibration   : Fluke Model 87V Sr. No. 43250126
Ref Meter used for calibration have valid calibration certificate.
             This is to certify that the above product has been tested as shown above and found to be working satisfactorily.

Tested by :                                                                                   

